## Slide 1
Chapter 6
Warehouse-Scale Computers to Exploit Request-Level and Data-Level Parallelism:
Computer Architecture
A Quantitative Approach, Fifth Edition

## Slide 2: Introduction
Warehouse-scale computer (WSC)
  Provides Internet services
    Search, social networking, online maps, video sharing, online shopping, email, cloud computing, etc.
  Differences with HPC “clusters”:
    Clusters have higher performance processors and network
    Clusters emphasize latency to complete a single task, WSCs emphasize request-level parallelism
  Differences with datacenters:
    Datacenters consolidate different machines and software into one location. Centrally provide HW&SW needs of an organization.
    Datacenters emphasize virtual machines and hardware heterogeneity in order to serve varied customers. WSCs tend to have homogeneous HW; support many less versatile tasks
Introduction

## Slide 3: Introduction
Important design factors for WSC:
  Cost-performance
    Small savings add up
  Energy efficiency
    Affects power distribution and cooling
    Work per joule
  Dependability via redundancy
  Network I/O
  Interactive and batch processing workloads
  Ample computational parallelism is not important
    Most jobs are totally independent
    “Request-level parallelism”
  Operational costs count
    Power consumption is a primary, not secondary, constraint when designing system
  Scale and its opportunities and problems
    Can afford to build customized systems since WSC require volume purchase
Introduction

## Slide 4: Prgrm’g Models and Workloads
In addition to “public-facing” internet services (search, video sharing, sorical networking) WSCs also run batch apps (convert videos into new format, create search indexes from Web crawlers)
Lead batch processing framework: MapReduce (using open-source Hadoop)
  Map: applies a programmer-supplied function to each logical input record
    Runs on thousands of computers
    Provides new set of key-value pairs as intermediate values
  Reduce: collapses values using another programmer-supplied function
Programming Models and Workloads for WSCs

## Slide 5: Prgrm’g Models and Workloads
Example:
  map (String key, String value):
    // key: document name
    // value: document contents
    for each word w in value
      Emit(w,”1”); // Produce list of all words
  reduce (String key, Iterator values):
    // key: a word
    // value: a list of counts
    int result = 0;
    for each v in values:
      result += ParseInt(v); // get integer from key-value pair
    Emit(word,result);
Programming Models and Workloads for WSCs
Each document is split into words, and each word is counted by the map function, using the word as the result key. The framework puts together all the pairs with the same key and feeds them to the same call to reduce, thus this function just needs to sum all of its input values to find the total appearances of that word

## Slide 6: Prgrm’g Models and Workloads
MapReduce runtime environment schedules map and reduce task to WSC nodes
Availability:
  Use replicas of data across different servers
  Use relaxed consistency:
    No need for all replicas to always agree. Only eventually. Makes storage system easier to scale – important for WSC.
Workload demands
  Often vary considerably
Programming Models and Workloads for WSCs

## Slide 7: Computer Architecture of WSC
WSC often use a hierarchy of networks for interconnection
Each 19” rack holds 48 1U (”rack units”)servers connected to a rack switch
Rack switches are uplinked to switch higher in hierarchy
  Uplink has 48 / n times lower bandwidth, where n = # of uplink ports
    “Oversubscription”
  Goal is to maximize locality of communication relative to the rack (programmer needs to know relative bandwidths)
Computer Ar4chitecture of WSC

## Slide 8: Storage
Storage options:
  Use disks inside the servers, or
  Network attached storage through Infiniband
  WSCs generally rely on local disks
  Google File System (GFS) uses local disks and maintains at least three relicas
Computer Ar4chitecture of WSC

## Slide 9: Array Switch
Switch that connects an array of racks
  Array switch should have 10 X the bisection bandwidth of rack switch
  Cost of n-port switch grows as n2
  Often utilize content addressible memory chips and FPGAs
  Much more expensive than 48-port commodity internet switch
Computer Ar4chitecture of WSC

## Slide 10: WSC Memory Hierarchy
Servers can access DRAM and disks on other servers using a NUMA-style interface
Computer Ar4chitecture of WSC

## Slide 11: Infrastructure and Costs of WSC
Location of WSC
  Proximity to Internet backbones, electricity cost, property tax rates, low risk from earthquakes, floods, and hurricanes
Power distribution and where losses occur
Physcical Infrastrcuture and Costs of WSC

## Slide 12: Infrastructure and Costs of WSC
Cooling
  Air conditioning used to cool server room
  64 F – 71 F
    Keep temperature higher (closer to 71 F)
  Cooling towers can also be used
    Minimum temperature is “wet bulb temperature”
    Mechanical design for cooling systems
Physcical Infrastrcuture and Costs of WSC

## Slide 13: Infrastructure and Costs of WSC
Cooling system also uses water (evaporation and spills)
  E.g. 70,000 to 200,000 gallons per day for an 8 MW facility
Power cost breakdown:
  Chillers: 30-50% of the power used by the IT equipment
  Air conditioning: 10-20% of the IT power, mostly due to fans
How many servers can a WSC support?
  Each server:
    “Nameplate power rating” gives maximum power consumption
    To get actual, measure power under actual workloads
  Oversubscribe cumulative server power by 40%, but monitor power closely
Physcical Infrastrcuture and Costs of WSC

## Slide 14: Measuring Efficiency of a WSC
Power Utilization Effectiveness (PEU)
  = Total facility power / IT equipment power
  Median PUE on 2006 study was 1.69
Performance
  Latency is important metric because it is seen by users
  Bing study: users will use search less as response time increases
  Service Level Objectives (SLOs)/Service Level Agreements (SLAs)
    E.g. 99% of requests be below 100 ms
Physcical Infrastrcuture and Costs of WSC

## Slide 15: Cost of a WSC
Capital expenditures (CAPEX)
  Cost to build a WSC
Operational expenditures (OPEX)
  Cost to operate a WSC
Physcical Infrastrcuture and Costs of WSC

## Slide 16: Cloud Computing
WSCs offer economies of scale that cannot be achieved with a datacenter:
  5.7 times reduction in storage costs
  7.1 times reduction in administrative costs
  7.3 times reduction in networking costs
  This has given rise to cloud services such as Amazon Web Services
    “Utility Computing”
    Based on using open source virtual machine and operating system software
Cloud Computing